## Instructions
13 · Hotel Preventive Maintenance Checklists: Daily Rounds to Annual, HVAC, Plumbing & Electrical
How to use this template:
▸ 7 checklists: daily round, weekly, monthly, quarterly & annual, HVAC, plumbing, electrical.
▸ Covers preventive and corrective maintenance for the hotel.
▸ Essential for code compliance and energy efficiency.
Customization:
▸ Adjust to the age and equipment of your hotel.
▸ Add any specific equipment in your facility.
Beyond the month:
▸ The "Quarterly & Annual" tab lists what is CONTRACTED and what an inspector asks for in writing: pest control, hoods (NFPA 96), food safety plan and training, calibration, Legionella (ASHRAE 188) and cooling towers, pool and spa water, sprinklers and fire alarm (NFPA 25 and 72), extinguishers (OSHA), gas, electrical (NFPA 70B), elevators and boilers (state or municipal inspector), evacuation drill, waste, insurance, I-9 and time records, PMS / POS and permits.
▸ The "Frequency" column already gives the legal or recommended frequency of each check; note the part number and the date of the next one in "Notes".
▸ Descaling coffee machines and hot water dispensers is monthly and goes on the "Monthly PM" tab; daily cleaning of the coffee group head is done by whoever uses the machine, in 01 (buffet) and 04 (lobby bar).
Designed by John Guerrero — chef and restaurant consultant since 2010, in professional kitchens since age 17 · johnguerrero.es
Version 2.0 · October 2026 · aichef.pro/en/digital-products/hotel-checklist-templates · info@aichef.pro

## Daily Rounds
Engineering — Daily Round
AI Chef Pro · aichef.pro — Hotel Checklists Kit Pro
Daily technical round (7:00–8:00 AM)
# | Task | Area | Assigned to | ✓ | Time | Notes
1 | Check boilers and domestic hot water production (140 °F or above in the storage tank, CDC) | Engineering
2 | Check the main electrical panels: no alarms or tripped breakers | Engineering
3 | Check the emergency generator: fuel level and standby status | Engineering
4 | Check HVAC temperatures in public areas and test rooms | Engineering
5 | Check water pumps (pressure, noise) | Engineering
6 | Visual round of public areas: lobby, corridors, facade | Engineering
7 | Review the work order list and prioritize today's repairs | Engineering
| Tasks done: | 0 | of | 7
Signed off by: _________________ Date: ___/___/______
© 2026 AI Chef Pro · aichef.pro

## Weekly PM
Engineering — Weekly Tasks
AI Chef Pro · aichef.pro — Hotel Checklists Kit Pro
Weekly checks
# | Task | Area | Assigned to | ✓ | Time | Notes
1 | Clean A/C filters in public areas (restaurant, lobby, ballrooms) | Engineering
2 | Check fire extinguishers (visual inspection, at least monthly, OSHA 1910.157(e)(2)) and standpipe hose cabinets: seals, gauge in the green and clear access | Engineering
3 | Test smoke detectors (rotating sample per floor) | Engineering
4 | Check elevators: doors, buttons, lighting | Engineering
5 | Lubricate emergency door hinges and check they close | Engineering
6 | Check pool and spa pumps: pressure, noise, leaks | Engineering
7 | Check emergency lighting (functional test): 30 seconds monthly and 90 minutes yearly, logged (NFPA 101 §7.9.3) | Engineering
8 | Read meters: water, gas, electricity (record consumption) | Engineering
| Tasks done: | 0 | of | 8
Signed off by: _________________ Date: ___/___/______
© 2026 AI Chef Pro · aichef.pro

## Monthly PM
Engineering — Monthly Tasks
AI Chef Pro · aichef.pro — Hotel Checklists Kit Pro
Monthly checks
# | Task | Area | Assigned to | ✓ | Time | Notes
1 | Check commercial kitchen equipment and exhaust hoods | Engineering
2 | Descale the coffee machines and hot water dispensers at all outlets (buffet, lobby bar, à la carte, in-room dining) or contract the service call, and replace the water softener filters on the supply line — record the date and part number | Engineering
3 | Inspect roofs, gutters and downspouts | Engineering
4 | Check the condition of exterior and interior paint (high-use areas) | Engineering
5 | Check fire doors: self-closing, magnetic hold-opens and signage; periodic inspection by a professional (NFPA 80) | Engineering
6 | Test the emergency generator under load monthly, as the manufacturer and your fire code specify | Engineering
7 | Check plumbing: drains, traps, possible leaks | Engineering
8 | Inspect guest room furniture: drawers, hinges, pulls | Engineering
9 | Update the maintenance log and plan next month | Admin
| Tasks done: | 0 | of | 9
Signed off by: _________________ Date: ___/___/______
© 2026 AI Chef Pro · aichef.pro

## Quarterly & Annual
Quarterly & Annual Maintenance — Contracted Services
AI Chef Pro · aichef.pro — Hotel Checklists Kit Pro
Food safety and pest control
# | Task | Area | Assigned to | ✓ | Frequency | Notes
1 | Pest control by a licensed pest management company: kitchens, storerooms, public areas and a rotating sample of guest rooms for bed bugs — service visit and signed service report on file | Engineering |  |  | Monthly
2 | Kitchen hood and duct cleaning by a certified contractor at the NFPA 96 frequency for your cooking volume (quarterly if high volume, semiannual if moderate): service report on file | Engineering |  |  | Semiannual
3 | Optional third-party food safety audit or ATP swab testing to verify your cleaning (many brands require an annual audit) | Engineering |  |  | Semiannual
4 | Review your food safety plan (HACCP if your health department or a variance requires one) and supplier approvals: the menu and buffet changes of the year | Admin |  |  | Annual
5 | Renew food handler cards and allergen training for all F&B staff, banquet extras included, and check a certified food protection manager is on the F&B management team (FDA Food Code 2-102.12; card rules vary by state) | Admin |  |  | Annual
6 | Calibrate the thermometers and probes of walk-ins, buffet and in-room dining in ice water (32 °F) and log any offset | Engineering |  |  | Quarterly
Water, Legionella, pool and spa
# | Task | Area | Assigned to | ✓ | Frequency | Notes
1 | Cooling towers and domestic hot water: cleaning and disinfection under your Legionella water management program (ASHRAE 188); cooling towers registered, inspected and tested where your state or city requires it (New York State and New York City do) | Engineering |  |  | Semiannual
2 | Legionella sampling by an accredited lab at the frequency your water management program sets; results logged and corrective actions recorded | Engineering |  |  | Quarterly
3 | Hot water temperature at outlets: stored at 140 °F or above and circulating at 120 °F or above (CDC); thermostatic mixing valves keep the guest outlets scald-safe; flush the outlets of rooms out of order or out of service for a week or more | Engineering |  |  | Quarterly
4 | Pool and spa water: lab or health-department testing where your state code requires it, on top of the free chlorine and pH log (MAHC 2024: before opening and every 2 or 4 hours) | Engineering |  |  | Quarterly
5 | Drain, deep-clean and inspect pool and spa shells, filters and showers; check every drain cover is VGB-compliant and within its service life (15 U.S.C. 8003) | Engineering |  |  | Annual
Facilities, fire and safety
# | Task | Area | Assigned to | ✓ | Frequency | Notes
1 | Fire sprinkler, standpipe and fire alarm inspections by a licensed fire protection company at the NFPA 25 and NFPA 72 intervals (quarterly and annual items): tags and reports on file | Engineering |  |  | Quarterly
2 | Annual extinguisher maintenance by a licensed fire protection company: new tag and record (OSHA 1910.157(e)(3)); hydrostatic tests as each extinguisher label says | Engineering |  |  | Annual
3 | Gas lines and kitchen appliance connections checked by a licensed pro, as often as your local code or gas utility requires | Engineering |  |  | Annual
4 | Electrical maintenance program (NFPA 70B): infrared scan of main panels and switchgear by a qualified electrician | Engineering |  |  | Annual
5 | Elevator and dumbwaiter inspection by a licensed elevator inspector, as your state or city requires (certificate posted in each car), on top of the monthly maintenance contract | Engineering |  |  | Annual
6 | Boilers and water heaters: inspection for the state boiler certificate where your state requires one; chiller and HVAC plant service with its report | Engineering |  |  | Annual
7 | Evacuation drill with every shift, as often as your local fire code requires, and review of the emergency action plan | Admin |  |  | Annual
8 | Used cooking oil pickup by a licensed recycler and hazardous waste (lamps, batteries, chemicals) by a licensed hauler: keep receipts and manifests | Engineering |  |  | Quarterly
Documentation, insurance and staff
# | Task | Area | Assigned to | ✓ | Frequency | Notes
1 | Review insurance: general liability, property, liquor liability, workers' comp and pool and spa coverage — insured values, capacities and covered activities | Admin |  |  | Annual
2 | File the quarter's time records (FLSA: time cards 2 years, payroll 3) and check every new hire has a Form I-9, seasonal and banquet extras included | Admin |  |  | Quarterly
3 | PMS and POS review: software updates, user permissions, sales and occupancy tax rates, and PCI DSS for card data | Admin |  |  | Annual
4 | Renew permits and licenses: business license, health permit for each food outlet, liquor license, pool and spa operating permit and, if you have one, outdoor dining permit | Admin |  |  | Annual
5 | Update recipe costing, menu prices and banquet rates with actual supplier prices | Admin |  |  | Quarterly
6 | Write the report number of each inspection and the date of the next one in "Notes" | Admin |  |  | Quarterly
| Tasks done: | 0 | of | 25
Signed off by: _________________ Date: ___/___/______
© 2026 AI Chef Pro · aichef.pro

## HVAC
HVAC — Heating, Cooling & Ventilation
AI Chef Pro · aichef.pro — Hotel Checklists Kit Pro
Climate control
# | Task | Area | Assigned to | ✓ | Time | Notes
1 | Check temperature setpoints by zone (rooms, lobby, ballrooms) | HVAC
2 | Monitor refrigerant pressures and alarms on the production units; staff never handle refrigerant: only an EPA 608 certified technician (40 CFR Part 82) | HVAC
3 | Clean fan coil filters quarterly (rotate by floors) | HVAC
4 | Check thermostats: room issues, calibration | HVAC
5 | Check ventilation and air exchange in interior areas | HVAC
6 | Record energy consumption and compare with the previous period | HVAC
| Tasks done: | 0 | of | 6
Signed off by: _________________ Date: ___/___/______
© 2026 AI Chef Pro · aichef.pro

## Plumbing
Plumbing — Control & Prevention
AI Chef Pro · aichef.pro — Hotel Checklists Kit Pro
Plumbing checks
# | Task | Area | Assigned to | ✓ | Time | Notes
1 | Check water pressure at the highest points of the building | Plumbing
2 | Legionella control: water management program per ASHRAE 188 and CDC guidance; hot water stored at 140 °F or above and circulating at 120 °F or above (CDC); thermostatic mixing valves at points of use against scalding | Plumbing
3 | Inspect mechanical rooms: leaks, moisture, corrosion | Plumbing
4 | Do preventive drain clearing in high-use areas | Plumbing
5 | Check toilet tanks: running water, mechanism, float | Plumbing
6 | Check room fixtures: drips, scale, operation; flush fixtures in unused rooms weekly (Legionella, CDC) | Plumbing
7 | Check radiators/heating: bleeding, leaks, thermostats | Plumbing
| Tasks done: | 0 | of | 7
Signed off by: _________________ Date: ___/___/______
© 2026 AI Chef Pro · aichef.pro

## Electrical
Electrical — Control & Safety
AI Chef Pro · aichef.pro — Hotel Checklists Kit Pro
Electrical checks
# | Task | Area | Assigned to | ✓ | Time | Notes
1 | Check secondary panels per floor: no tripped breakers or alarms | Electrical
2 | Check emergency lighting and evacuation signs | Electrical
3 | Check LED fixtures: replace burned-out ones, check dimmers | Electrical
4 | Check outlets in rooms and public areas | Electrical
5 | Check electronic locks: batteries, programming, backup | Electrical
6 | Check the PA and background music system | Electrical
7 | Check EV chargers if any | Electrical
| Tasks done: | 0 | of | 7
Signed off by: _________________ Date: ___/___/______
© 2026 AI Chef Pro · aichef.pro